## CR
Components | Fragility Database Identifiers | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit | Cost Quantity (Imperial) |  | Cost Quantity (Metric) |  | Unit Cost, DS1 | Unit Cost, DS2 | Unit Cost, DS3 | Unit Cost, DS4 | Unit Cost, DS5
Cladding - Gross Wall Area | B2022.001 | 2 | 0.071535 | 0.040103 | 0.020439 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 1370 | 1370 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal |  |  |  | 30 | SF | 2.7871 | SM | 491.5519 | 491.5519
Cladding - Windows & Glazing Area | B2022.001 | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 1370 | 1370 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal |  |  |  | 30 | SF | 2.7871 | SM | 491.5519 | 491.5519
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 754
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 347
Floor Finishes including Raised Access Floors | C3021.001k | 8 | 0.212 | 0.042 | 0.0024 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 29.4 |  |  |  |  | 0.35 |  |  |  |  | Normal |  |  |  |  | 1 | SF | 0.092903 | SM | 316.459
Floor Finishes. Raised Access Floors and Floor Flooding | C3027.001 | 8 | 0 | 0.75 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 115 |  |  |  |  | 1.28 |  |  |  |  | Lognormal |  |  |  |  | 100 | SF | 9.2903 | SM | 12.3785
Roofing | B3011.014 | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 625 | 1030 |  |  |  | 0.64 | 0.43 |  |  |  | Lognormal | Lognormal |  |  |  | 100 | SF | 9.2903 | SM | 67.2744 | 110.8683
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 4 | PSD | 0.0018 | 0.0046 | 0.0105 | 0.0188 |  | 0.52 | 0.54 | 0.4 | 0.38 |  | 62 | 117 | 234 | 234 |  | 0.4814 | 0.5559 | 0.1959 |  |  | Lognormal | Lognormal |  |  |  | 10.7639 | SF | 1 | SM | 62 | 117 | 234 | 234
Ceramic tile walls | C3011.001a; C3011.002a | 2 | 0.011631 | 0.0047915 | 0.00013167 | 2 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 7200 | 29160 |  |  |  | 0.22 | 0.09 |  |  |  | Lognormal | Lognormal |  |  |  | 900 | SF | 83.6127 | SM | 86.1113 | 348.7507
Ceilings - Lay in Tile | C3032.001a | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 362.5 | 2837.5 | 5837.5 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal |  |  | 250 | SF | 23.2258 | SM | 15.6077 | 122.1704 | 251.3373
Ceilings - Gypsum board | C3032.001a | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 362.5 | 2837.5 | 5837.5 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal |  |  | 250 | SF | 23.2258 | SM | 15.6077 | 122.1704 | 251.3373
Ceilings - Other | C3032.001a | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 362.5 | 2837.5 | 5837.5 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal |  |  | 250 | SF | 23.2258 | SM | 15.6077 | 122.1704 | 251.3373
Ceilings - Other (high end) | C3032.001a | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 362.5 | 2837.5 | 5837.5 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal |  |  | 250 | SF | 23.2258 | SM | 15.6077 | 122.1704 | 251.3373
Stairs | C2011.021b | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.005 | 0.017 | 0.028 |  |  | 0.6 | 0.6 | 0.45 |  |  | 700 | 3700 | 24950 |  |  | 0.8015 | 0.5694 | 0.34 |  |  | Lognormal | Lognormal | Normal |  |  | 1 | EA | 1 | EA | 700 | 3700 | 24950
Elevators | D1014.011 | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4400 | 18700 | 16000 | 2500 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877 |  | Lognormal | Normal | Normal | Normal |  | 1 | EA | 1 | EA | 4400 | 18700 | 16000 | 2500 | 0
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 290 | 2650 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 0.95144 | 8.6942
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 350 | 3350 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 1.1483 | 10.9908
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 290 | 2650 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 0.95144 | 8.6942
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 350 | 3350 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 1.1483 | 10.9908
Piping - Sanitary Waste Piping | D2031.011b | 7 | 0.036881 | 0.023165 | 0.006035 | 2 | PFA | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | 400 | 2850 |  |  |  | 0.58 | 0.34 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 1.3123 | 9.3504
Piping - Acid Waste Piping | D2061.021a | 7 | 0 | 0.013716 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 350 | 3350 |  |  |  | 0.65 | 0.4 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 1.1483 | 10.9908
HVAC - Chiller capacity | D3031.011a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 46200 |  |  |  |  | 0.1785 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 46200
HVAC - Cooling Tower capacity | D3031.021a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 23700 |  |  |  |  | 0.172 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 23700
HVAC - Air Handling Units | D3052.011a | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1000 | 29200 |  |  |  | 0.1511 | 0.1655 |  |  |  | Lognormal | Lognormal |  |  |  | 1 | EA | 1 | EA | 1000 | 29200
HVAC - Fans | D3041.101a | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2650 |  |  |  |  | 0.1394 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 2650
HVAC - HVAC Ducts – 6 sq. feet for larger | D3041.012a | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 950 | 7950 |  |  |  | 0.256 | 0.0806 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 3.1168 | 26.0827
HVAC - HVAC Ducts – less than 6 sq. feet | D3041.011a | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 650 | 5750 |  |  |  | 0.3674 | 0.1002 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 2.1325 | 18.8648
HVAC - HVAC in-line Drops & Diffusers | D3041.031a | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 3000 |  |  |  |  | 0.2066 |  |  |  |  | Normal |  |  |  |  | 10 | Units | 10 | Units | 300
HVAC - HVAC in-line Coils | D3041.041a | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 15000 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal |  |  |  |  | 10 | Units | 10 | Units | 1500
HVAC - VAV Boxes | D3041.041a | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 15000 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal |  |  |  |  | 10 | Units | 10 | Units | 1500
HVAC - Fan Coil Unis | D3041.041a | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 15000 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal |  |  |  |  | 10 | Units | 10 | Units | 1500
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D2051.011a | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 290 | 2650 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 0.95144 | 8.6942
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D2051.021a | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 350 | 3350 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 1.1483 | 10.9908
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D2022.011a | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 290 | 2650 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 0.95144 | 8.6942
Piping - Heating Water Piping – greater than 2 ½ diameter | D2022.021a | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 350 | 3350 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 1.1483 | 10.9908
Electrical - Motor Control Centers | D5012.013a | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4150 |  |  |  |  | 0.1826 |  |  |  |  | Normal |  |  |  |  | 1 | EA | 1 | EA | 4150
Electrical - Transformers < 100kVA | D5011.011a | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 7575 |  |  |  |  | 0.1875 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 7575 | 0
Electrical - Distribution Panel | D5012.031a | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 9275 | 0
Electrical - Wall mounted switchgear | D5012.021a | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 9275 | 0
Electrical - Lighting Fixtures – Lay in fluorescent | C3034.001 | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 495 | 0
Electrical - Lighting Fixtures – Stem hung fluorescent | C3034.001 | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal |  |  |  |  | 1 | EA | 1 | EA | 495 | 0
Electrical - Standby generators | D5092.031a | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 200 | 2500 | 500 | 500 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673 |  | Lognormal | Lognormal | Lognormal | Lognormal |  | 1 | EA | 1 | EA | 200 | 2500 | 500 | 500
Fire Protection - Sprinkler Piping | D4011.021a | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 350 | 2650 |  |  |  | 0.6488 | 0.4054 |  |  |  | Lognormal | Lognormal |  |  |  | 1000 | LF | 304.8 | LM | 1.1483 | 8.6942
Fire Protection - Sprinkler Drops | D4011.031a | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 500 | 500 |  |  |  | 0.3665 | 0.3665 |  |  |  | Lognormal | Lognormal |  |  |  | 100 | Units | 100 | Units | 5 | 5
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0.28228 | 0.20172 | 0.11432 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal |  |  |  | 1 | LM | 51.3 | 73.5 | 199.9 | 234
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0.11919 | 0.074816 | 0.039875 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal |  |  |  | 1 | LM | 51.3 | 73.5 | 199.9 | 234

## MCF
Components | Fragility Database Identifiers | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 2 | 0.071535 | 0.040103 | 0.020439 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3
Roofing | B301 Roof Coverings | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 132.9386 | 250.2691 |  |  |  | 0.5149 | 0.4691
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 3 | PSD | 0.5 | 1 | 2.1 |  |  | 0.4 | 0.3 | 0.2 |  |  | 22.1702 | 56.5124 | 86.9421 |  |  | 0.4814 | 0.5559 | 0.1959
Ceramic tile walls | C301 Wall Finishes | 2 | 0.011631 | 0.0047915 | 0.00013167 | 1 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 85.9689 | 364.6037 |  |  |  | 0.22 | 0.09
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Stairs | C201 Stairs | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.5 | 1.7 | 2.8 |  |  | 0.6 | 0.6 | 0.45 |  |  | 280 | 1480 | 9180 |  |  | 0.8015 | 0.5694 | 0.3613
Elevators | D101 Elevators & Lifts | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4434.7814 | 22567.9176 | 36901.1436 | 38901.1425 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Gas supply piping | D301 Energy Supply | 7 | 0.012192 | 0.009652 | 0.004572 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 11.4829 |  |  |  |  | 0.65
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 7 | 0.036881 | 0.023165 | 0.006035 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 7 | 0 | 0.013716 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 47847.4484 |  |  |  |  | 0.1785
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 26070 |  |  |  |  | 0.172
HVAC - Air Handling Units | D305 Control Panels | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1100 | 32120 |  |  |  | 0.1511 | 0.1655
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2915 |  |  |  |  | 0.1394
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.4285 | 28.6909 |  |  |  | 0.256 | 0.0806
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.3458 | 22.9167 |  |  |  | 0.3674 | 0.1002
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 330 |  |  |  |  | 0.2066
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.20932 | 1.9127 |  |  |  | 0.7637 | 0.4054
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Electrical - Electrical Load | D501 Electrical Service & Distribution | 5 | 3.4747 | 4.6736 | 1.8288 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 5 | 0.06096 | 0.06096 | 0.03048 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 5 | 0 | 0.002032 | 0 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 8332.5 |  |  |  |  | 0.1875
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 12057.5 |  |  |  |  | 0.1572
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 10202.5 |  |  |  |  | 0.1572
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Standby generators | D509 Other Electrical Systems | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 220 | 3470 | 4070 | 4670 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 0.42104 | 3.1879 |  |  |  | 0.6488 | 0.4054
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 2.75 | 2.75 |  |  |  | 0.3665 | 0.3665
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0.28228 | 0.20172 | 0.11432 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0.11919 | 0.074816 | 0.039875 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55

## URM
Components | Fragility Database Identifiers | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 2 | 0.071535 | 0.040103 | 0.020439 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3
Roofing | B301 Roof Coverings | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 132.9386 | 250.2691 |  |  |  | 0.5149 | 0.4691
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 3 | PSD | 0.5 | 1 | 2.1 |  |  | 0.4 | 0.3 | 0.2 |  |  | 22.1702 | 56.5124 | 86.9421 |  |  | 0.4814 | 0.5559 | 0.1959
Ceramic tile walls | C301 Wall Finishes | 2 | 0.011631 | 0.0047915 | 0.00013167 | 1 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 85.9689 | 364.6037 |  |  |  | 0.22 | 0.09
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Stairs | C201 Stairs | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.5 | 1.7 | 2.8 |  |  | 0.6 | 0.6 | 0.45 |  |  | 280 | 1480 | 9180 |  |  | 0.8015 | 0.5694 | 0.3613
Elevators | D101 Elevators & Lifts | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4434.7814 | 22567.9176 | 36901.1436 | 38901.1425 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Gas supply piping | D301 Energy Supply | 7 | 0.012192 | 0.009652 | 0.004572 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 11.4829 |  |  |  |  | 0.65
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 7 | 0.036881 | 0.023165 | 0.006035 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 7 | 0 | 0.013716 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 47847.4484 |  |  |  |  | 0.1785
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 26070 |  |  |  |  | 0.172
HVAC - Air Handling Units | D305 Control Panels | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1100 | 32120 |  |  |  | 0.1511 | 0.1655
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2915 |  |  |  |  | 0.1394
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.4285 | 28.6909 |  |  |  | 0.256 | 0.0806
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.3458 | 22.9167 |  |  |  | 0.3674 | 0.1002
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 330 |  |  |  |  | 0.2066
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.20932 | 1.9127 |  |  |  | 0.7637 | 0.4054
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Electrical - Electrical Load | D501 Electrical Service & Distribution | 5 | 3.4747 | 4.6736 | 1.8288 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 5 | 0.06096 | 0.06096 | 0.03048 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 5 | 0 | 0.002032 | 0 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 8332.5 |  |  |  |  | 0.1875
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 12057.5 |  |  |  |  | 0.1572
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 10202.5 |  |  |  |  | 0.1572
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Standby generators | D509 Other Electrical Systems | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 220 | 3470 | 4070 | 4670 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 0.42104 | 3.1879 |  |  |  | 0.6488 | 0.4054
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 2.75 | 2.75 |  |  |  | 0.3665 | 0.3665
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0 | 0 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0 | 0 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55

## S
Components | Fragility Database Identifiers | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 2 | 0.071535 | 0.040103 | 0.020439 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3
Roofing | B301 Roof Coverings | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 132.9386 | 250.2691 |  |  |  | 0.5149 | 0.4691
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 3 | PSD | 0.5 | 1 | 2.1 |  |  | 0.4 | 0.3 | 0.2 |  |  | 22.1702 | 56.5124 | 86.9421 |  |  | 0.4814 | 0.5559 | 0.1959
Ceramic tile walls | C301 Wall Finishes | 2 | 0.011631 | 0.0047915 | 0.00013167 | 1 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 85.9689 | 364.6037 |  |  |  | 0.22 | 0.09
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Stairs | C201 Stairs | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.5 | 1.7 | 2.8 |  |  | 0.6 | 0.6 | 0.45 |  |  | 280 | 1480 | 9180 |  |  | 0.8015 | 0.5694 | 0.3613
Elevators | D101 Elevators & Lifts | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4434.7814 | 22567.9176 | 36901.1436 | 38901.1425 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Gas supply piping | D301 Energy Supply | 7 | 0.012192 | 0.009652 | 0.004572 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 11.4829 |  |  |  |  | 0.65
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 7 | 0.036881 | 0.023165 | 0.006035 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 7 | 0 | 0.013716 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 47847.4484 |  |  |  |  | 0.1785
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 26070 |  |  |  |  | 0.172
HVAC - Air Handling Units | D305 Control Panels | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1100 | 32120 |  |  |  | 0.1511 | 0.1655
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2915 |  |  |  |  | 0.1394
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.4285 | 28.6909 |  |  |  | 0.256 | 0.0806
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.3458 | 22.9167 |  |  |  | 0.3674 | 0.1002
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 330 |  |  |  |  | 0.2066
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.20932 | 1.9127 |  |  |  | 0.7637 | 0.4054
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Electrical - Electrical Load | D501 Electrical Service & Distribution | 5 | 3.4747 | 4.6736 | 1.8288 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 5 | 0.06096 | 0.06096 | 0.03048 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 5 | 0 | 0.002032 | 0 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 8332.5 |  |  |  |  | 0.1875
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 12057.5 |  |  |  |  | 0.1572
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 10202.5 |  |  |  |  | 0.1572
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Standby generators | D509 Other Electrical Systems | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 220 | 3470 | 4070 | 4670 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 0.42104 | 3.1879 |  |  |  | 0.6488 | 0.4054
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 2.75 | 2.75 |  |  |  | 0.3665 | 0.3665
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0.28228 | 0.20172 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0.11919 | 0.074816 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55

## T
Components | Fragility Database Identifiers | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 2 | 0.071535 | 0.040103 | 0.020439 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3
Roofing | B301 Roof Coverings | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 132.9386 | 250.2691 |  |  |  | 0.5149 | 0.4691
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 3 | PSD | 0.5 | 1 | 2.1 |  |  | 0.4 | 0.3 | 0.2 |  |  | 22.1702 | 56.5124 | 86.9421 |  |  | 0.4814 | 0.5559 | 0.1959
Ceramic tile walls | C301 Wall Finishes | 2 | 0.011631 | 0.0047915 | 0.00013167 | 1 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 85.9689 | 364.6037 |  |  |  | 0.22 | 0.09
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Stairs | C201 Stairs | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.5 | 1.7 | 2.8 |  |  | 0.6 | 0.6 | 0.45 |  |  | 280 | 1480 | 9180 |  |  | 0.8015 | 0.5694 | 0.3613
Elevators | D101 Elevators & Lifts | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4434.7814 | 22567.9176 | 36901.1436 | 38901.1425 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Gas supply piping | D301 Energy Supply | 7 | 0.012192 | 0.009652 | 0.004572 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 11.4829 |  |  |  |  | 0.65
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 7 | 0.036881 | 0.023165 | 0.006035 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 7 | 0 | 0.013716 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 47847.4484 |  |  |  |  | 0.1785
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 26070 |  |  |  |  | 0.172
HVAC - Air Handling Units | D305 Control Panels | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1100 | 32120 |  |  |  | 0.1511 | 0.1655
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2915 |  |  |  |  | 0.1394
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.4285 | 28.6909 |  |  |  | 0.256 | 0.0806
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.3458 | 22.9167 |  |  |  | 0.3674 | 0.1002
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 330 |  |  |  |  | 0.2066
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.20932 | 1.9127 |  |  |  | 0.7637 | 0.4054
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Electrical - Electrical Load | D501 Electrical Service & Distribution | 5 | 3.4747 | 4.6736 | 1.8288 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 5 | 0.06096 | 0.06096 | 0.03048 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 5 | 0 | 0.002032 | 0 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 8332.5 |  |  |  |  | 0.1875
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 12057.5 |  |  |  |  | 0.1572
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 10202.5 |  |  |  |  | 0.1572
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Standby generators | D509 Other Electrical Systems | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 220 | 3470 | 4070 | 4670 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 0.42104 | 3.1879 |  |  |  | 0.6488 | 0.4054
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 2.75 | 2.75 |  |  |  | 0.3665 | 0.3665
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0 | 0 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0 | 0 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55

## ADO
Components | Fragility Database Identifiers | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 2 | 0.071535 | 0.040103 | 0.020439 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 1 | PSD | 0.0338 |  |  |  |  | 0.4 |  |  |  |  | 102.75 |  |  |  |  | 0.17
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 1.88 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3
Roofing | B301 Roof Coverings | 8 | 0 | 0 | 0 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 132.9386 | 250.2691 |  |  |  | 0.5149 | 0.4691
Gypsum Partitions | Sassun et al. | 1 | 0.22 | 0.3 | 0.15 | 3 | PSD | 0.5 | 1 | 2.1 |  |  | 0.4 | 0.3 | 0.2 |  |  | 22.1702 | 56.5124 | 86.9421 |  |  | 0.4814 | 0.5559 | 0.1959
Ceramic tile walls | C301 Wall Finishes | 2 | 0.011631 | 0.0047915 | 0.00013167 | 1 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 85.9689 | 364.6037 |  |  |  | 0.22 | 0.09
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 0.86 | 1.3275 | 1.5625 |  |  | 0.25 | 0.25 | 0.25 |  |  | 18.6937 | 146.3264 | 301.0326 |  |  | 0.5508 | 0.5183 | 0.2026
Stairs | C201 Stairs | 4 | 0 | 0 | 0 | 3 | PSD | 0.5 | 1.7 | 2.8 |  |  | 0.6 | 0.6 | 0.45 |  |  | 280 | 1480 | 9180 |  |  | 0.8015 | 0.5694 | 0.3613
Elevators | D101 Elevators & Lifts | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4434.7814 | 22567.9176 | 36901.1436 | 38901.1425 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Gas supply piping | D301 Energy Supply | 7 | 0.012192 | 0.009652 | 0.004572 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 11.4829 |  |  |  |  | 0.65
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 7 | 0.036881 | 0.023165 | 0.006035 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 7 | 0 | 0 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 7 | 0 | 0.013716 | 0 | 1 | PFA | 2.25 |  |  |  |  | 0.5 |  |  |  |  | 4.3963 |  |  |  |  | 0.3142
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 47847.4484 |  |  |  |  | 0.1785
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 26070 |  |  |  |  | 0.172
HVAC - Air Handling Units | D305 Control Panels | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1100 | 32120 |  |  |  | 0.1511 | 0.1655
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2915 |  |  |  |  | 0.1394
HVAC - HVAC Ducts – 6 sq. feet or larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.4285 | 28.6909 |  |  |  | 0.256 | 0.0806
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.3458 | 22.9167 |  |  |  | 0.3674 | 0.1002
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 330 |  |  |  |  | 0.2066
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1650 |  |  |  |  | 0.2942
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.20932 | 1.9127 |  |  |  | 0.7637 | 0.4054
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 1.0466 | 9.5636 |  |  |  | 0.7637 | 0.4054
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 0.45932 | 4.3963 |  |  |  | 0.6488 | 0.4038
Electrical - Electrical Load | D501 Electrical Service & Distribution | 5 | 3.4747 | 4.6736 | 1.8288 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 5 | 0.06096 | 0.06096 | 0.03048 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 5 | 0 | 0.002032 | 0 | 1 | PFA | 1 |  |  |  |  | 0.4 |  |  |  |  | 12.1458 |  |  |  |  | 0.2
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4565 |  |  |  |  | 0.1826
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 8332.5 |  |  |  |  | 0.1875
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 12057.5 |  |  |  |  | 0.1572
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 10202.5 |  |  |  |  | 0.1572
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 0.46 |  |  |  |  | 0.6369
Electrical - Standby generators | D509 Other Electrical Systems | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 220 | 3470 | 4070 | 4670 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0 | 0 | 0 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 0.42104 | 3.1879 |  |  |  | 0.6488 | 0.4054
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 8 | 0 | 0 | 0 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 2.75 | 2.75 |  |  |  | 0.3665 | 0.3665
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0 | 0 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0 | 0 | 0 | 4 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 0.30351 | 0.5268 | 1.793 | 1.9884 |  | 0.55 | 0.55 | 0.55 | 0.55