## cr
Components | Fragility Referencews | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B2022.001 | 2 | 0.071535 | 0.040103 | 0.020439 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B2022.001 | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Floor Finishes including Raised Access Floors | C3021.001k | 8 | 0.212 | 0.042 | 0.0024 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 316.459 |  |  |  |  | 0.35 |  |  |  |  | Normal
Floor Finishes. Raised Access Floors and Floor Flooding | C3027.001 | 8 | 0 | 0.75 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 12.3785 |  |  |  |  | 1.28 |  |  |  |  | Lognormal
Roofing | B3011.014 | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 67.2744 | 110.8683 |  |  |  | 0.64 | 0.43 |  |  |  | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 4 | PSD | 0.0018 | 0.0046 | 0.0105 | 0.0188 |  | 0.52 | 0.54 | 0.4 | 0.38 |  | 62 | 117 | 234 | 234 |  | 0.4814 | 0.5559 | 0.1959 | 0.1959 |  | Lognormal | Lognormal
Ceramic tile walls | C3011.001a; C3011.002a | 2 | 0.011631 | 0.0047915 | 0.00013167 | 2 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 86.1113 | 348.7507 |  |  |  | 0.22 | 0.09 |  |  |  | Lognormal | Lognormal
Ceilings - Lay in Tile | C3032.001a | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C3032.001a | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other | C3032.001a | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C3032.001a | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Stairs | C2011.021b | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.005 | 0.017 | 0.028 |  |  | 0.6 | 0.6 | 0.45 |  |  | 700 | 3700 | 24950 |  |  | 0.8015 | 0.5694 | 0.34 |  |  | Lognormal | Lognormal | Normal
Elevators | D1014.011 | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4400 | 23100 | 39100 | 41600 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877 |  | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Sanitary Waste Piping | D2031.011b | 7 | 0.036881 | 0.023165 | 0.006035 | 2 | PFA | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | 1.3123 | 9.3504 |  |  |  | 0.58 | 0.34 |  |  |  | Lognormal | Lognormal
Piping - Acid Waste Piping | D2061.021a | 7 | 0 | 0.013716 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.65 | 0.4 |  |  |  | Lognormal | Lognormal
HVAC - Chiller capacity | D3031.011a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 46200 |  |  |  |  | 0.1785 |  |  |  |  | Lognormal
HVAC - Cooling Tower capacity | D3031.021a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 23700 |  |  |  |  | 0.172 |  |  |  |  | Lognormal
HVAC - Air Handling Units | D3052.011a | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1000 | 29200 |  |  |  | 0.1511 | 0.1655 |  |  |  | Lognormal | Lognormal
HVAC - Fans | D3041.101a | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2650 |  |  |  |  | 0.1394 |  |  |  |  | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D3041.012a | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.1168 | 26.0827 |  |  |  | 0.256 | 0.0806 |  |  |  | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D3041.011a | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.1325 | 18.8648 |  |  |  | 0.3674 | 0.1002 |  |  |  | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D3041.031a | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 300 |  |  |  |  | 0.2066 |  |  |  |  | Normal
HVAC - HVAC in-line Coils | D3041.041a | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - VAV Boxes | D3041.041a | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - Fan Coil Unis | D3041.041a | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D2051.011a | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D2051.021a | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D2022.011a | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D2022.021a | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Electrical - Motor Control Centers | D5012.013a | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4150 |  |  |  |  | 0.1826 |  |  |  |  | Normal
Electrical - Transformers < 100kVA | D5011.011a | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 7575 |  |  |  |  | 0.1875 |  |  |  |  | Lognormal
Electrical - Distribution Panel | D5012.031a | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Wall mounted switchgear | D5012.021a | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C3034.001 | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C3034.001 | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Standby generators | D5092.031a | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 200 | 2500 | 500 | 500 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673 |  | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D4011.021a | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 1.1483 | 8.6942 |  |  |  | 0.6488 | 0.4054 |  |  |  | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D4011.031a | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 5 | 5 |  |  |  | 0.3665 | 0.3665 |  |  |  | Lognormal | Lognormal
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0.28228 | 0.20172 | 0.11432 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0.11919 | 0.074816 | 0.039875 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal

## mur
Components | Fragility Referencews | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B2022.001 | 2 | 0.071535 | 0.040103 | 0.020439 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B2022.001 | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Floor Finishes including Raised Access Floors | C3021.001k | 8 | 0.212 | 0.042 | 0.0024 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 316.459 |  |  |  |  | 0.35 |  |  |  |  | Normal
Floor Finishes. Raised Access Floors and Floor Flooding | C3027.001 | 8 | 0 | 0.75 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 12.3785 |  |  |  |  | 1.28 |  |  |  |  | Lognormal
Roofing | B3011.014 | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 67.2744 | 110.8683 |  |  |  | 0.64 | 0.43 |  |  |  | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 4 | PSD | 0.0018 | 0.0046 | 0.0105 | 0.0188 |  | 0.52 | 0.54 | 0.4 | 0.38 |  | 62 | 117 | 234 | 234 |  | 0.4814 | 0.5559 | 0.1959 | 0.1959 |  | Lognormal | Lognormal
Ceramic tile walls | C3011.001a; C3011.002a | 2 | 0.011631 | 0.0047915 | 0.00013167 | 2 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 86.1113 | 348.7507 |  |  |  | 0.22 | 0.09 |  |  |  | Lognormal | Lognormal
Ceilings - Lay in Tile | C3032.001a | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C3032.001a | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other | C3032.001a | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C3032.001a | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Stairs | C2011.021b | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.005 | 0.017 | 0.028 |  |  | 0.6 | 0.6 | 0.45 |  |  | 700 | 3700 | 24950 |  |  | 0.8015 | 0.5694 | 0.34 |  |  | Lognormal | Lognormal | Normal
Elevators | D1014.011 | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4400 | 23100 | 39100 | 41600 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877 |  | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Sanitary Waste Piping | D2031.011b | 7 | 0.036881 | 0.023165 | 0.006035 | 2 | PFA | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | 1.3123 | 9.3504 |  |  |  | 0.58 | 0.34 |  |  |  | Lognormal | Lognormal
Piping - Acid Waste Piping | D2061.021a | 7 | 0 | 0.013716 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.65 | 0.4 |  |  |  | Lognormal | Lognormal
HVAC - Chiller capacity | D3031.011a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 46200 |  |  |  |  | 0.1785 |  |  |  |  | Lognormal
HVAC - Cooling Tower capacity | D3031.021a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 23700 |  |  |  |  | 0.172 |  |  |  |  | Lognormal
HVAC - Air Handling Units | D3052.011a | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1000 | 29200 |  |  |  | 0.1511 | 0.1655 |  |  |  | Lognormal | Lognormal
HVAC - Fans | D3041.101a | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2650 |  |  |  |  | 0.1394 |  |  |  |  | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D3041.012a | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.1168 | 26.0827 |  |  |  | 0.256 | 0.0806 |  |  |  | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D3041.011a | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.1325 | 18.8648 |  |  |  | 0.3674 | 0.1002 |  |  |  | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D3041.031a | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 300 |  |  |  |  | 0.2066 |  |  |  |  | Normal
HVAC - HVAC in-line Coils | D3041.041a | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - VAV Boxes | D3041.041a | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - Fan Coil Unis | D3041.041a | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D2051.011a | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D2051.021a | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D2022.011a | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D2022.021a | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Electrical - Motor Control Centers | D5012.013a | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4150 |  |  |  |  | 0.1826 |  |  |  |  | Normal
Electrical - Transformers < 100kVA | D5011.011a | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 7575 |  |  |  |  | 0.1875 |  |  |  |  | Lognormal
Electrical - Distribution Panel | D5012.031a | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Wall mounted switchgear | D5012.021a | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C3034.001 | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C3034.001 | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Standby generators | D5092.031a | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 200 | 2500 | 500 | 500 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673 |  | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D4011.021a | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 1.1483 | 8.6942 |  |  |  | 0.6488 | 0.4054 |  |  |  | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D4011.031a | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 5 | 5 |  |  |  | 0.3665 | 0.3665 |  |  |  | Lognormal | Lognormal
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0 | 0 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0 | 0 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal

## mcf
Components | Fragility Referencews | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B2022.001 | 2 | 0.071535 | 0.040103 | 0.020439 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B2022.001 | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Floor Finishes including Raised Access Floors | C3021.001k | 8 | 0.212 | 0.042 | 0.0024 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 316.459 |  |  |  |  | 0.35 |  |  |  |  | Normal
Floor Finishes. Raised Access Floors and Floor Flooding | C3027.001 | 8 | 0 | 0.75 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 12.3785 |  |  |  |  | 1.28 |  |  |  |  | Lognormal
Roofing | B3011.014 | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 67.2744 | 110.8683 |  |  |  | 0.64 | 0.43 |  |  |  | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 4 | PSD | 0.0018 | 0.0046 | 0.0105 | 0.0188 |  | 0.52 | 0.54 | 0.4 | 0.38 |  | 62 | 117 | 234 | 234 |  | 0.4814 | 0.5559 | 0.1959 | 0.1959 |  | Lognormal | Lognormal
Ceramic tile walls | C3011.001a; C3011.002a | 2 | 0.011631 | 0.0047915 | 0.00013167 | 2 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 86.1113 | 348.7507 |  |  |  | 0.22 | 0.09 |  |  |  | Lognormal | Lognormal
Ceilings - Lay in Tile | C3032.001a | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C3032.001a | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other | C3032.001a | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C3032.001a | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Stairs | C2011.021b | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.005 | 0.017 | 0.028 |  |  | 0.6 | 0.6 | 0.45 |  |  | 700 | 3700 | 24950 |  |  | 0.8015 | 0.5694 | 0.34 |  |  | Lognormal | Lognormal | Normal
Elevators | D1014.011 | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4400 | 23100 | 39100 | 41600 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877 |  | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Sanitary Waste Piping | D2031.011b | 7 | 0.036881 | 0.023165 | 0.006035 | 2 | PFA | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | 1.3123 | 9.3504 |  |  |  | 0.58 | 0.34 |  |  |  | Lognormal | Lognormal
Piping - Acid Waste Piping | D2061.021a | 7 | 0 | 0.013716 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.65 | 0.4 |  |  |  | Lognormal | Lognormal
HVAC - Chiller capacity | D3031.011a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 46200 |  |  |  |  | 0.1785 |  |  |  |  | Lognormal
HVAC - Cooling Tower capacity | D3031.021a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 23700 |  |  |  |  | 0.172 |  |  |  |  | Lognormal
HVAC - Air Handling Units | D3052.011a | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1000 | 29200 |  |  |  | 0.1511 | 0.1655 |  |  |  | Lognormal | Lognormal
HVAC - Fans | D3041.101a | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2650 |  |  |  |  | 0.1394 |  |  |  |  | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D3041.012a | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.1168 | 26.0827 |  |  |  | 0.256 | 0.0806 |  |  |  | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D3041.011a | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.1325 | 18.8648 |  |  |  | 0.3674 | 0.1002 |  |  |  | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D3041.031a | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 300 |  |  |  |  | 0.2066 |  |  |  |  | Normal
HVAC - HVAC in-line Coils | D3041.041a | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - VAV Boxes | D3041.041a | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - Fan Coil Unis | D3041.041a | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D2051.011a | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D2051.021a | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D2022.011a | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D2022.021a | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Electrical - Motor Control Centers | D5012.013a | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4150 |  |  |  |  | 0.1826 |  |  |  |  | Normal
Electrical - Transformers < 100kVA | D5011.011a | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 7575 |  |  |  |  | 0.1875 |  |  |  |  | Lognormal
Electrical - Distribution Panel | D5012.031a | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Wall mounted switchgear | D5012.021a | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C3034.001 | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C3034.001 | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Standby generators | D5092.031a | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 200 | 2500 | 500 | 500 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673 |  | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D4011.021a | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 1.1483 | 8.6942 |  |  |  | 0.6488 | 0.4054 |  |  |  | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D4011.031a | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 5 | 5 |  |  |  | 0.3665 | 0.3665 |  |  |  | Lognormal | Lognormal
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0.28228 | 0.20172 | 0.11432 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0.11919 | 0.074816 | 0.039875 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal

## w
Components | Fragility Referencews | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B2022.001 | 2 | 0.071535 | 0.040103 | 0.020439 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B2022.001 | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Floor Finishes including Raised Access Floors | C3021.001k | 8 | 0.212 | 0.042 | 0.0024 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 316.459 |  |  |  |  | 0.35 |  |  |  |  | Normal
Floor Finishes. Raised Access Floors and Floor Flooding | C3027.001 | 8 | 0 | 0.75 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 12.3785 |  |  |  |  | 1.28 |  |  |  |  | Lognormal
Roofing | B3011.014 | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 67.2744 | 110.8683 |  |  |  | 0.64 | 0.43 |  |  |  | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 4 | PSD | 0.0018 | 0.0046 | 0.0105 | 0.0188 |  | 0.52 | 0.54 | 0.4 | 0.38 |  | 62 | 117 | 234 | 234 |  | 0.4814 | 0.5559 | 0.1959 | 0.1959 |  | Lognormal | Lognormal
Ceramic tile walls | C3011.001a; C3011.002a | 2 | 0.011631 | 0.0047915 | 0.00013167 | 2 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 86.1113 | 348.7507 |  |  |  | 0.22 | 0.09 |  |  |  | Lognormal | Lognormal
Ceilings - Lay in Tile | C3032.001a | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C3032.001a | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other | C3032.001a | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C3032.001a | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Stairs | C2011.021b | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.005 | 0.017 | 0.028 |  |  | 0.6 | 0.6 | 0.45 |  |  | 700 | 3700 | 24950 |  |  | 0.8015 | 0.5694 | 0.34 |  |  | Lognormal | Lognormal | Normal
Elevators | D1014.011 | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4400 | 23100 | 39100 | 41600 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877 |  | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Sanitary Waste Piping | D2031.011b | 7 | 0.036881 | 0.023165 | 0.006035 | 2 | PFA | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | 1.3123 | 9.3504 |  |  |  | 0.58 | 0.34 |  |  |  | Lognormal | Lognormal
Piping - Acid Waste Piping | D2061.021a | 7 | 0 | 0.013716 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.65 | 0.4 |  |  |  | Lognormal | Lognormal
HVAC - Chiller capacity | D3031.011a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 46200 |  |  |  |  | 0.1785 |  |  |  |  | Lognormal
HVAC - Cooling Tower capacity | D3031.021a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 23700 |  |  |  |  | 0.172 |  |  |  |  | Lognormal
HVAC - Air Handling Units | D3052.011a | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1000 | 29200 |  |  |  | 0.1511 | 0.1655 |  |  |  | Lognormal | Lognormal
HVAC - Fans | D3041.101a | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2650 |  |  |  |  | 0.1394 |  |  |  |  | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D3041.012a | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.1168 | 26.0827 |  |  |  | 0.256 | 0.0806 |  |  |  | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D3041.011a | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.1325 | 18.8648 |  |  |  | 0.3674 | 0.1002 |  |  |  | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D3041.031a | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 300 |  |  |  |  | 0.2066 |  |  |  |  | Normal
HVAC - HVAC in-line Coils | D3041.041a | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - VAV Boxes | D3041.041a | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - Fan Coil Unis | D3041.041a | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D2051.011a | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D2051.021a | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D2022.011a | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D2022.021a | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Electrical - Motor Control Centers | D5012.013a | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4150 |  |  |  |  | 0.1826 |  |  |  |  | Normal
Electrical - Transformers < 100kVA | D5011.011a | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 7575 |  |  |  |  | 0.1875 |  |  |  |  | Lognormal
Electrical - Distribution Panel | D5012.031a | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Wall mounted switchgear | D5012.021a | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C3034.001 | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C3034.001 | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Standby generators | D5092.031a | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 200 | 2500 | 500 | 500 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673 |  | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D4011.021a | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 1.1483 | 8.6942 |  |  |  | 0.6488 | 0.4054 |  |  |  | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D4011.031a | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 5 | 5 |  |  |  | 0.3665 | 0.3665 |  |  |  | Lognormal | Lognormal
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0 | 0 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0 | 0 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal

## s
Components | Fragility Referencews | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B2022.001 | 2 | 0.071535 | 0.040103 | 0.020439 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B2022.001 | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Floor Finishes including Raised Access Floors | C3021.001k | 8 | 0.212 | 0.042 | 0.0024 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 316.459 |  |  |  |  | 0.35 |  |  |  |  | Normal
Floor Finishes. Raised Access Floors and Floor Flooding | C3027.001 | 8 | 0 | 0.75 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 12.3785 |  |  |  |  | 1.28 |  |  |  |  | Lognormal
Roofing | B3011.014 | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 67.2744 | 110.8683 |  |  |  | 0.64 | 0.43 |  |  |  | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 0.21 | 0.18 | 0.03 | 4 | PSD | 0.0018 | 0.0046 | 0.0105 | 0.0188 |  | 0.52 | 0.54 | 0.4 | 0.38 |  | 62 | 117 | 234 | 234 |  | 0.4814 | 0.5559 | 0.1959 | 0.1959 |  | Lognormal | Lognormal
Ceramic tile walls | C3011.001a; C3011.002a | 2 | 0.011631 | 0.0047915 | 0.00013167 | 2 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 86.1113 | 348.7507 |  |  |  | 0.22 | 0.09 |  |  |  | Lognormal | Lognormal
Ceilings - Lay in Tile | C3032.001a | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C3032.001a | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other | C3032.001a | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C3032.001a | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Stairs | C2011.021b | 4 | 0.00012 | 0.00010333 | 0 | 3 | PSD | 0.005 | 0.017 | 0.028 |  |  | 0.6 | 0.6 | 0.45 |  |  | 700 | 3700 | 24950 |  |  | 0.8015 | 0.5694 | 0.34 |  |  | Lognormal | Lognormal | Normal
Elevators | D1014.011 | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4400 | 23100 | 39100 | 41600 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877 |  | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Sanitary Waste Piping | D2031.011b | 7 | 0.036881 | 0.023165 | 0.006035 | 2 | PFA | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | 1.3123 | 9.3504 |  |  |  | 0.58 | 0.34 |  |  |  | Lognormal | Lognormal
Piping - Acid Waste Piping | D2061.021a | 7 | 0 | 0.013716 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.65 | 0.4 |  |  |  | Lognormal | Lognormal
HVAC - Chiller capacity | D3031.011a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 46200 |  |  |  |  | 0.1785 |  |  |  |  | Lognormal
HVAC - Cooling Tower capacity | D3031.021a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 23700 |  |  |  |  | 0.172 |  |  |  |  | Lognormal
HVAC - Air Handling Units | D3052.011a | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1000 | 29200 |  |  |  | 0.1511 | 0.1655 |  |  |  | Lognormal | Lognormal
HVAC - Fans | D3041.101a | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2650 |  |  |  |  | 0.1394 |  |  |  |  | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D3041.012a | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.1168 | 26.0827 |  |  |  | 0.256 | 0.0806 |  |  |  | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D3041.011a | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.1325 | 18.8648 |  |  |  | 0.3674 | 0.1002 |  |  |  | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D3041.031a | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 300 |  |  |  |  | 0.2066 |  |  |  |  | Normal
HVAC - HVAC in-line Coils | D3041.041a | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - VAV Boxes | D3041.041a | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - Fan Coil Unis | D3041.041a | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D2051.011a | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D2051.021a | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D2022.011a | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D2022.021a | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Electrical - Motor Control Centers | D5012.013a | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4150 |  |  |  |  | 0.1826 |  |  |  |  | Normal
Electrical - Transformers < 100kVA | D5011.011a | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 7575 |  |  |  |  | 0.1875 |  |  |  |  | Lognormal
Electrical - Distribution Panel | D5012.031a | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Wall mounted switchgear | D5012.021a | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C3034.001 | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C3034.001 | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Standby generators | D5092.031a | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 200 | 2500 | 500 | 500 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673 |  | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D4011.021a | 8 | 0.067056 | 0.06096 | 0.033528 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 1.1483 | 8.6942 |  |  |  | 0.6488 | 0.4054 |  |  |  | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D4011.031a | 8 | 0.012 | 0.0096667 | 0.008 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 5 | 5 |  |  |  | 0.3665 | 0.3665 |  |  |  | Lognormal | Lognormal
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0.28228 | 0.20172 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0.11919 | 0.074816 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal

## ado
Components | Fragility Referencews | Performance Group | Residential | Commercial | Industrial | Damage States | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS5, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS5, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS5, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | DS5, COST Dispersion (Beta) | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit | DS5, best fit
Cladding - Gross Wall Area | B2022.001 | 2 | 0.071535 | 0.040103 | 0.020439 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B2022.001 | 3 | 0.013935 | 0.014864 | 9.2903e-05 | 2 | PSD | 0.0338 | 0.0383 |  |  |  | 0.4 | 0.4 |  |  |  | 491.5519 | 491.5519 |  |  |  | 0.17 | 0.17 |  |  |  | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 3 | 0.15 | 0.15 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 754 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 3 | 0.22 | 0.3 | 0.15 | 1 | PSD | 0.0188 |  |  |  |  | 0.38 |  |  |  |  | 347 |  |  |  |  | 0.3 |  |  |  |  | Lognormal
Floor Finishes including Raised Access Floors | C3021.001k | 8 | 0.212 | 0.042 | 0.0024 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 316.459 |  |  |  |  | 0.35 |  |  |  |  | Normal
Floor Finishes. Raised Access Floors and Floor Flooding | C3027.001 | 8 | 0 | 0.75 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.5 |  |  |  |  | 12.3785 |  |  |  |  | 1.28 |  |  |  |  | Lognormal
Roofing | B3011.014 | 8 | 0.029729 | 0.030039 | 0.092903 | 2 | PFA | 0.4 | 0.5 |  |  |  | 0.3 | 0.3 |  |  |  | 67.2744 | 110.8683 |  |  |  | 0.64 | 0.43 |  |  |  | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 0.432 | 1.092 | 0.1524 | 4 | PSD | 0.0018 | 0.0046 | 0.0105 | 0.0188 |  | 0.52 | 0.54 | 0.4 | 0.38 |  | 62 | 117 | 234 | 234 |  | 0.4814 | 0.5559 | 0.1959 | 0.1959 |  | Lognormal | Lognormal
Ceramic tile walls | C3011.001a; C3011.002a | 2 | 0.011631 | 0.0047915 | 0.00013167 | 2 | PSD | 0.0021 | 0.0071 |  |  |  | 0.6 | 0.45 |  |  |  | 86.1113 | 348.7507 |  |  |  | 0.22 | 0.09 |  |  |  | Lognormal | Lognormal
Ceilings - Lay in Tile | C3032.001a | 8 | 0 | 0.060387 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C3032.001a | 8 | 0.088258 | 0.024155 | 0.0046452 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other | C3032.001a | 8 | 0.0046452 | 0.0040258 | 0.083613 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C3032.001a | 8 | 0 | 0.0043355 | 0 | 3 | PFA | 1.17 | 1.58 | 1.82 |  |  | 0.25 | 0.25 | 0.25 |  |  | 15.6077 | 122.1704 | 251.3373 |  |  | 0.5508 | 0.5183 | 0.2026 |  |  | Normal | Lognormal | Lognormal
Stairs | C2011.021b | 4 | 0 | 0 | 0 | 3 | PSD | 0.005 | 0.017 | 0.028 |  |  | 0.6 | 0.6 | 0.45 |  |  | 700 | 3700 | 24950 |  |  | 0.8015 | 0.5694 | 0.34 |  |  | Lognormal | Lognormal | Normal
Elevators | D1014.011 | 5 | 0.00049239 | 0.00020284 | 0 | 4 | PFA | 0.39 | 0.39 | 0.39 | 0.39 |  | 0.45 | 0.45 | 0.45 | 0.45 |  | 4400 | 23100 | 39100 | 41600 |  | 0.8741 | 0.2776 | 0.4083 | 0.4877 |  | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.032309 | 0.015443 | 0.001463 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.004572 | 0.004572 | 0.004572 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D2021.011a | 7 | 0.064618 | 0.030886 | 0.0029261 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D2021.021a | 7 | 0.009144 | 0.009144 | 0.009144 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.64877 | 0.40381 |  |  |  | Lognormal | Lognormal
Piping - Sanitary Waste Piping | D2031.011b | 7 | 0.036881 | 0.023165 | 0.006035 | 2 | PFA | 1.2 | 2.4 |  |  |  | 0.5 | 0.5 |  |  |  | 1.3123 | 9.3504 |  |  |  | 0.58 | 0.34 |  |  |  | Lognormal | Lognormal
Piping - Acid Waste Piping | D2061.021a | 7 | 0 | 0.013716 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.65 | 0.4 |  |  |  | Lognormal | Lognormal
HVAC - Chiller capacity | D3031.011a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.2 |  |  |  |  | 0.4 |  |  |  |  | 46200 |  |  |  |  | 0.1785 |  |  |  |  | Lognormal
HVAC - Cooling Tower capacity | D3031.021a | 6 | 0 | 0.00028956 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 23700 |  |  |  |  | 0.172 |  |  |  |  | Lognormal
HVAC - Air Handling Units | D3052.011a | 6 | 0 | 0.0066073 | 0.0056634 | 2 | PFA | 0.25 | 0.25 |  |  |  | 0.4 | 0.4 |  |  |  | 1000 | 29200 |  |  |  | 0.1511 | 0.1655 |  |  |  | Lognormal | Lognormal
HVAC - Fans | D3041.101a | 6 | 0 | 0 | 0 | 1 | PFA | 0.5 |  |  |  |  | 0.4 |  |  |  |  | 2650 |  |  |  |  | 0.1394 |  |  |  |  | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D3041.012a | 6 | 0 | 0.007112 | 0 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 3.1168 | 26.0827 |  |  |  | 0.256 | 0.0806 |  |  |  | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D3041.011a | 6 | 0.01524 | 0.013208 | 0.012192 | 2 | PFA | 1.5 | 2.25 |  |  |  | 0.4 | 0.4 |  |  |  | 2.1325 | 18.8648 |  |  |  | 0.3674 | 0.1002 |  |  |  | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D3041.031a | 6 | 0.008 | 0.0056667 | 0.003 | 1 | PFA | 1.3 |  |  |  |  | 0.4 |  |  |  |  | 300 |  |  |  |  | 0.2066 |  |  |  |  | Normal
HVAC - HVAC in-line Coils | D3041.041a | 6 | 0 | 0.0016667 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - VAV Boxes | D3041.041a | 6 | 0 | 0.002 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
HVAC - Fan Coil Unis | D3041.041a | 6 | 0.004 | 0.006 | 0 | 1 | PFA | 1.9 |  |  |  |  | 0.4 |  |  |  |  | 1500 |  |  |  |  | 0.2942 |  |  |  |  | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D2051.011a | 7 | 0 | 0 | 0 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D2051.021a | 7 | 0 | 0.000508 | 0 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.5 | 0.5 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D2022.011a | 7 | 0.001524 | 0.003556 | 0.001524 | 2 | PFA | 0.55 | 1.1 |  |  |  | 0.5 | 0.5 |  |  |  | 0.95144 | 8.6942 |  |  |  | 0.7637 | 0.4054 |  |  |  | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D2022.021a | 7 | 0.001524 | 0.001524 | 0.001524 | 2 | PFA | 1.5 | 2.6 |  |  |  | 0.4 | 0.4 |  |  |  | 1.1483 | 10.9908 |  |  |  | 0.6488 | 0.4038 |  |  |  | Lognormal | Lognormal
Electrical - Motor Control Centers | D5012.013a | 5 | 0 | 1.3333e-05 | 0 | 1 | PFA | 0.73 |  |  |  |  | 0.45 |  |  |  |  | 4150 |  |  |  |  | 0.1826 |  |  |  |  | Normal
Electrical - Transformers < 100kVA | D5011.011a | 5 | 5e-05 | 0.0001 | 5e-05 | 1 | PFA | 1.01 |  |  |  |  | 0.6 |  |  |  |  | 7575 |  |  |  |  | 0.1875 |  |  |  |  | Lognormal
Electrical - Distribution Panel | D5012.031a | 5 | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | PFA | 2.16 |  |  |  |  | 0.45 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Wall mounted switchgear | D5012.021a | 5 | 0.0008 | 0.0003 | 0.0001 | 1 | PFA | 1.28 |  |  |  |  | 0.4 |  |  |  |  | 9275 |  |  |  |  | 0.1572 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C3034.001 | 5 | 0 | 0.01 | 0 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C3034.001 | 5 | 0 | 0.01 | 0.015 | 1 | PFA | 0.6 |  |  |  |  | 0.4 |  |  |  |  | 495 |  |  |  |  | 0.6369 |  |  |  |  | Lognormal
Electrical - Standby generators | D5092.031a | 5 | 0 | 0 | 0 | 4 | PFA | 0.9 | 0.9 | 0.9 | 0.9 |  | 0.4 | 0.4 | 0.4 | 0.4 |  | 200 | 2500 | 500 | 500 |  | 0.1713 | 0.1705 | 0.1673 | 0.1673 |  | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D4011.021a | 8 | 0 | 0 | 0 | 2 | PFA | 1.1 | 2.4 |  |  |  | 0.4 | 0.5 |  |  |  | 1.1483 | 8.6942 |  |  |  | 0.6488 | 0.4054 |  |  |  | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D4011.031a | 8 | 0 | 0 | 0 | 2 | PFA | 0.75 | 0.95 |  |  |  | 0.4 | 0.4 |  |  |  | 5 | 5 |  |  |  | 0.3665 | 0.3665 |  |  |  | Lognormal | Lognormal
External Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 2 | 0 | 0 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal
Internal Partitioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 0 | 0 | 0 | 4 | PSD | 0.000992 | 0.004092 | 0.012028 | 0.021328 |  | 0.8 | 0.4 | 0.4 | 0.4 |  | 51.3 | 73.5 | 199.9 | 234 |  | 0.55 | 0.55 | 0.55 | 0.55 |  | Lognormal | Lognormal | Lognormal | Lognormal