## CR
Components | Fragility Database Identifiers | Cost Multiplier (to unit metric) | Quantity unit | RESIDENTIAL - METRIC | COMMERCIAL - METRIC | INDUSTRIAL - METRIC | Damage States | Performance Group | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | Damage Type | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 1 | Each | 0.071535 | 0.040103 | 0.020439 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 1 | Each | 0.013935 | 0.014864 | 9.2903e-05 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.15 | 0.15 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 754 | 0 | 0 | 0 | 0.3 |  |  |  | Mutually exclusive | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.22 | 0.3 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 347 | 0 | 0 | 0 | 0.3
Roofing | B301 Roof Coverings | 9.29 | 100 SF | 0.029729 | 0.030039 | 0.092903 | 2 | 2 | PFA | 0.4 | 0.5 | NA | NA | 0.3 | 0.3 | NA | NA | 132.9386 | 250.2691 | 0 | 0 | 0.5149 | 0.4691 | NA | NA | Sequential | Lognormal | Lognormal
Interior Partitions | C101 Partitions | 120.77 | 1300 SF | 0.036576 | 0.017272 | 0.0009144 | 3 | 1 | PSD | 0.005 | 0.01 | 0.021 | NA | 0.4 | 0.3 | 0.2 | NA | 22.1702 | 56.5124 | 86.9421 | 0 | 0.4814 | 0.5559 | 0.1959 | NA | Sequential | Normal | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 1 | 0.21 | 0.18 | 0.03 | 4 | 1 | PSD | 0.18 | 0.46 | 1.05 | 1.88 | 0.52 | 0.54 | 0.4 | 0.38 | 0.31 | 0.59 | 1.18 | 1.18 | 0.5508 | 0.5183
Ceramic tile walls | C301 Wall Finishes | 1 | Each | 0.011631 | 0.0047915 | 0.00013167 | 1 | 1 | PSD | 0.0021 | NA | NA | NA | 0.6 | NA | NA | NA | 3240 | 0 | 0 | 0 | 0.1542 | NA | NA | NA | Sequential | Lognormal
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.060387 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.088258 | 0.024155 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.0046452 | 0.0040258 | 0.083613 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.0043355 | 0 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Storage Racks | F101 Special Structures including Storage Racks | 15.24 | 50 LF | 0 | 0 | 0.03048 | 2 | 2 | PFA | 0.42 | 0.42 | NA | NA | 0.4 | 0.4 | NA | NA | 15.6471 | 94.1349 | 0 | 0 | 0.3622 | 0.2881 | NA | NA | Mutually exclusive | Lognormal | Lognormal
Stairs | C201 Stairs | 1 | Each | 0.00012 | 0.00010333 | 0 | 3 | 1 | PSD | 0.005 | 0.017 | 0.028 | NA | 0.6 | 0.6 | 0.45 | NA | 280 | 1480 | 9180 | 0 | 0.8015 | 0.5694 | 0.3613 | NA | Sequential | Lognormal | Lognormal | Normal
Elevators | D101 Elevators & Lifts | 1 | Each | 3.4e-05 | 4.7667e-05 | 0 | 4 | 2 | PFA | 0.39 | 0.39 | 0.39 | 0.39 | 0.45 | 0.45 | 0.45 | 0.45 | 1760 | 7480 | 6400 | 1000 | 0.8741 | 0.2776 | 0.4083 | 0.4877 | Simultaneous | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.032309 | 0.015443 | 0.001463 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.004572 | 0.004572 | 0.004572 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.064618 | 0.030886 | 0.0029261 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.009144 | 0.009144 | 0.009144 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Gas supply piping | D301 Energy Supply | 304.8 | 1000 LF | 0.012192 | 0.009652 | 0.004572 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 11.4829 | 0 | 0 | 0 | 0.65 |  |  |  |  | Normal
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0.036881 | 0.023165 | 0.006035 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0.013716 | 0 |  | 2 | [9 empty] | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 50820 | 0 | 0 | 0 | 0.1785 | NA | NA | NA | Sequential | Lognormal
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 26070 | 0 | 0 | 0 | 0.172 | NA | NA | NA | Sequential | Lognormal
HVAC - Boiler capacity | D302 Heat Generating Systems (furnaces and boilers) | 1 | Each | 45 | 45 | 15 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 46200 | 0 | 0 | 0 | 0.18 | NA | NA | NA | Sequential | Lognormal
HVAC - Air Handling Units | D305 Control Panels | 1 | Each | 0 | 0.0066073 | 0.0056634 | 1 | 2 | PFA | 0.25 | 0.25 | NA | NA | 0.4 | 0.4 | NA | NA | 1100 | 32120 | 0 | 0 | 0.1511 | 0.1655 | NA | NA | Mutually exclusive | Lognormal
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 1 | Each | 0 | 0 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 2915 | 0 | 0 | 0 | 0.1394 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0 | 0.007112 | 0 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 3.4285 | 28.6909 | 0 | 0 | 0.256 | 0.0806 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0.01524 | 0.013208 | 0.012192 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 2.3458 | 22.9167 | 0 | 0 | 0.3674 | 0.1002 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.008 | 0.0056667 | 0.003 | 1 | 2 | PFA | 1.3 | NA | NA | NA | 0.4 | NA | NA | NA | 330 | 0 | 0 | 0 | 0.2066 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.0016667 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Normal
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.002 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.004 | 0.006 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0 | 0 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 0.20932 | 1.9127 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0.000508 | 0 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.003556 | 0.001524 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.001524 | 0.001524 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Electrical - Electrical Load | D501 Electrical Service & Distribution | 1 | Each | 3.4747 | 4.6736 | 1.8288 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 1 | Each | 0.06096 | 0.06096 | 0.03048 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 1 | Each | 0 | 0.002032 | 0 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 1 | Each | 0 | 1.3333e-05 | 0 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 1 | Each | 5e-05 | 0.0001 | 5e-05 | 1 | 2 | PFA | 1.01 | NA | NA | NA | 0.6 | NA | NA | NA | 8332.5 | 0 | 0 | 0 | 0.1875 | NA | NA | NA | Sequential | Lognormal
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 1 | Each | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | 2 | PFA | 2.16 | NA | NA | NA | 0.45 | NA | NA | NA | 12057.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 1 | Each | 0.0008 | 0.0003 | 0.0001 | 1 | 2 | PFA | 1.28 | NA | NA | NA | 0.4 | NA | NA | NA | 10202.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0.015 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Standby generators | D509 Other Electrical Systems | 1 | Each | 0 | 0 | 0 | 4 | 2 | PFA | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4 | 0.4 | 220 | 3250 | 600 | 600 | 0.1713 | 0.1705 | 0.1673 | 0.1673 | Mutually exclusive | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 304.8 | 1000 LF | 0.067056 | 0.06096 | 0.033528 | 2 | 2 | PFA | 1.1 | 2.4 | NA | NA | 0.4 | 0.5 | NA | NA | 0.42104 | 3.1879 | 0 | 0 | 0.6488 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 100 | 100 Units | 0.012 | 0.0096667 | 0.008 | 2 | 2 | PFA | 0.75 | 0.95 | NA | NA | 0.4 | 0.4 | NA | NA | 2.75 | 2.75 | 0 | 0 | 0.3665 | 0.3665 | NA | NA | Sequential | Lognormal | Lognormal
Exterenal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0.28228 | 0.20172 | 0.11432 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal
Internal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0.11919 | 0.074816 | 0.039875 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal

## MCF
Components | Fragility Database Identifiers | Cost Multiplier (to unit metric) | Quantity unit | RESIDENTIAL - METRIC | COMMERCIAL - METRIC | INDUSTRIAL - METRIC | Damage States | Performance Group | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | Damage Type | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 1 | Each | 0.071535 | 0.040103 | 0.020439 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 1 | Each | 0.013935 | 0.014864 | 9.2903e-05 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.15 | 0.15 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 754 | 0 | 0 | 0 | 0.3 |  |  |  | Mutually exclusive | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.22 | 0.3 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 347 | 0 | 0 | 0 | 0.3
Roofing | B301 Roof Coverings | 9.29 | 100 SF | 0.029729 | 0.030039 | 0.092903 | 2 | 2 | PFA | 0.4 | 0.5 | NA | NA | 0.3 | 0.3 | NA | NA | 132.9386 | 250.2691 | 0 | 0 | 0.5149 | 0.4691 | NA | NA | Sequential | Lognormal | Lognormal
Interior Partitions | C101 Partitions | 120.77 | 1300 SF | 0.036576 | 0.017272 | 0.0009144 | 3 | 1 | PSD | 0.005 | 0.01 | 0.021 | NA | 0.4 | 0.3 | 0.2 | NA | 22.1702 | 56.5124 | 86.9421 | 0 | 0.4814 | 0.5559 | 0.1959 | NA | Sequential | Normal | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 1 | 0.21 | 0.18 | 0.03 | 4 | 1 | PSD | 0.18 | 0.46 | 1.05 | 1.88 | 0.52 | 0.54 | 0.4 | 0.38 | 0.31 | 0.59 | 1.18 | 1.18 | 0.5508 | 0.5183
Ceramic tile walls | C301 Wall Finishes | 1 | Each | 0.011631 | 0.0047915 | 0.00013167 | 1 | 1 | PSD | 0.0021 | NA | NA | NA | 0.6 | NA | NA | NA | 3240 | 0 | 0 | 0 | 0.1542 | NA | NA | NA | Sequential | Lognormal
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.060387 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.088258 | 0.024155 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.0046452 | 0.0040258 | 0.083613 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.0043355 | 0 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Storage Racks | F101 Special Structures including Storage Racks | 15.24 | 50 LF | 0 | 0 | 0.03048 | 2 | 2 | PFA | 0.42 | 0.42 | NA | NA | 0.4 | 0.4 | NA | NA | 15.6471 | 94.1349 | 0 | 0 | 0.3622 | 0.2881 | NA | NA | Mutually exclusive | Lognormal | Lognormal
Stairs | C201 Stairs | 1 | Each | 0.00012 | 0.00010333 | 0 | 3 | 1 | PSD | 0.005 | 0.017 | 0.028 | NA | 0.6 | 0.6 | 0.45 | NA | 280 | 1480 | 9180 | 0 | 0.8015 | 0.5694 | 0.3613 | NA | Sequential | Lognormal | Lognormal | Normal
Elevators | D101 Elevators & Lifts | 1 | Each | 3.4e-05 | 4.7667e-05 | 0 | 4 | 2 | PFA | 0.39 | 0.39 | 0.39 | 0.39 | 0.45 | 0.45 | 0.45 | 0.45 | 1760 | 7480 | 6400 | 1000 | 0.8741 | 0.2776 | 0.4083 | 0.4877 | Simultaneous | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.032309 | 0.015443 | 0.001463 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.004572 | 0.004572 | 0.004572 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.064618 | 0.030886 | 0.0029261 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.009144 | 0.009144 | 0.009144 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Gas supply piping | D301 Energy Supply | 304.8 | 1000 LF | 0.012192 | 0.009652 | 0.004572 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 11.4829 | 0 | 0 | 0 | 0.65 |  |  |  |  | Normal
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0.036881 | 0.023165 | 0.006035 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0.013716 | 0 |  | 2 | [9 empty] | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 50820 | 0 | 0 | 0 | 0.1785 | NA | NA | NA | Sequential | Lognormal
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 26070 | 0 | 0 | 0 | 0.172 | NA | NA | NA | Sequential | Lognormal
HVAC - Boiler capacity | D302 Heat Generating Systems (furnaces and boilers) | 1 | Each | 45 | 45 | 15 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 46200 | 0 | 0 | 0 | 0.18 | NA | NA | NA | Sequential | Lognormal
HVAC - Air Handling Units | D305 Control Panels | 1 | Each | 0 | 0.0066073 | 0.0056634 | 1 | 2 | PFA | 0.25 | 0.25 | NA | NA | 0.4 | 0.4 | NA | NA | 1100 | 32120 | 0 | 0 | 0.1511 | 0.1655 | NA | NA | Mutually exclusive | Lognormal
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 1 | Each | 0 | 0 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 2915 | 0 | 0 | 0 | 0.1394 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0 | 0.007112 | 0 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 3.4285 | 28.6909 | 0 | 0 | 0.256 | 0.0806 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0.01524 | 0.013208 | 0.012192 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 2.3458 | 22.9167 | 0 | 0 | 0.3674 | 0.1002 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.008 | 0.0056667 | 0.003 | 1 | 2 | PFA | 1.3 | NA | NA | NA | 0.4 | NA | NA | NA | 330 | 0 | 0 | 0 | 0.2066 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.0016667 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Normal
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.002 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.004 | 0.006 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0 | 0 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 0.20932 | 1.9127 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0.000508 | 0 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.003556 | 0.001524 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.001524 | 0.001524 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Electrical - Electrical Load | D501 Electrical Service & Distribution | 1 | Each | 3.4747 | 4.6736 | 1.8288 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 1 | Each | 0.06096 | 0.06096 | 0.03048 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 1 | Each | 0 | 0.002032 | 0 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 1 | Each | 0 | 1.3333e-05 | 0 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 1 | Each | 5e-05 | 0.0001 | 5e-05 | 1 | 2 | PFA | 1.01 | NA | NA | NA | 0.6 | NA | NA | NA | 8332.5 | 0 | 0 | 0 | 0.1875 | NA | NA | NA | Sequential | Lognormal
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 1 | Each | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | 2 | PFA | 2.16 | NA | NA | NA | 0.45 | NA | NA | NA | 12057.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 1 | Each | 0.0008 | 0.0003 | 0.0001 | 1 | 2 | PFA | 1.28 | NA | NA | NA | 0.4 | NA | NA | NA | 10202.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0.015 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Standby generators | D509 Other Electrical Systems | 1 | Each | 0 | 0 | 0 | 4 | 2 | PFA | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4 | 0.4 | 220 | 3250 | 600 | 600 | 0.1713 | 0.1705 | 0.1673 | 0.1673 | Mutually exclusive | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 304.8 | 1000 LF | 0.067056 | 0.06096 | 0.033528 | 2 | 2 | PFA | 1.1 | 2.4 | NA | NA | 0.4 | 0.5 | NA | NA | 0.42104 | 3.1879 | 0 | 0 | 0.6488 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 100 | 100 Units | 0.012 | 0.0096667 | 0.008 | 2 | 2 | PFA | 0.75 | 0.95 | NA | NA | 0.4 | 0.4 | NA | NA | 2.75 | 2.75 | 0 | 0 | 0.3665 | 0.3665 | NA | NA | Sequential | Lognormal | Lognormal
Exterenal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0.28228 | 0.20172 | 0.11432 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal
Internal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0.11919 | 0.074816 | 0.039875 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal

## URM
Components | Fragility Database Identifiers | Cost Multiplier (to unit metric) | Quantity unit | RESIDENTIAL - METRIC | COMMERCIAL - METRIC | INDUSTRIAL - METRIC | Damage States | Performance Group | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | Damage Type | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 1 | Each | 0.071535 | 0.040103 | 0.020439 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 1 | Each | 0.013935 | 0.014864 | 9.2903e-05 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.15 | 0.15 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 754 | 0 | 0 | 0 | 0.3 |  |  |  | Mutually exclusive | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.22 | 0.3 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 347 | 0 | 0 | 0 | 0.3
Roofing | B301 Roof Coverings | 9.29 | 100 SF | 0.029729 | 0.030039 | 0.092903 | 2 | 2 | PFA | 0.4 | 0.5 | NA | NA | 0.3 | 0.3 | NA | NA | 132.9386 | 250.2691 | 0 | 0 | 0.5149 | 0.4691 | NA | NA | Sequential | Lognormal | Lognormal
Interior Partitions | C101 Partitions | 120.77 | 1300 SF | 0.036576 | 0.017272 | 0.0009144 | 3 | 1 | PSD | 0.005 | 0.01 | 0.021 | NA | 0.4 | 0.3 | 0.2 | NA | 22.1702 | 56.5124 | 86.9421 | 0 | 0.4814 | 0.5559 | 0.1959 | NA | Sequential | Normal | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 1 | 0.21 | 0.18 | 0.03 | 4 | 1 | PSD | 0.18 | 0.46 | 1.05 | 1.88 | 0.52 | 0.54 | 0.4 | 0.38 | 0.31 | 0.59 | 1.18 | 1.18 | 0.5508 | 0.5183
Ceramic tile walls | C301 Wall Finishes | 1 | Each | 0.011631 | 0.0047915 | 0.00013167 | 1 | 1 | PSD | 0.0021 | NA | NA | NA | 0.6 | NA | NA | NA | 3240 | 0 | 0 | 0 | 0.1542 | NA | NA | NA | Sequential | Lognormal
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.060387 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.088258 | 0.024155 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.0046452 | 0.0040258 | 0.083613 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.0043355 | 0 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Storage Racks | F101 Special Structures including Storage Racks | 15.24 | 50 LF | 0 | 0 | 0.03048 | 2 | 2 | PFA | 0.42 | 0.42 | NA | NA | 0.4 | 0.4 | NA | NA | 15.6471 | 94.1349 | 0 | 0 | 0.3622 | 0.2881 | NA | NA | Mutually exclusive | Lognormal | Lognormal
Stairs | C201 Stairs | 1 | Each | 0.00012 | 0.00010333 | 0 | 3 | 1 | PSD | 0.005 | 0.017 | 0.028 | NA | 0.6 | 0.6 | 0.45 | NA | 280 | 1480 | 9180 | 0 | 0.8015 | 0.5694 | 0.3613 | NA | Sequential | Lognormal | Lognormal | Normal
Elevators | D101 Elevators & Lifts | 1 | Each | 3.4e-05 | 4.7667e-05 | 0 | 4 | 2 | PFA | 0.39 | 0.39 | 0.39 | 0.39 | 0.45 | 0.45 | 0.45 | 0.45 | 1760 | 7480 | 6400 | 1000 | 0.8741 | 0.2776 | 0.4083 | 0.4877 | Simultaneous | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.032309 | 0.015443 | 0.001463 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.004572 | 0.004572 | 0.004572 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.064618 | 0.030886 | 0.0029261 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.009144 | 0.009144 | 0.009144 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Gas supply piping | D301 Energy Supply | 304.8 | 1000 LF | 0.012192 | 0.009652 | 0.004572 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 11.4829 | 0 | 0 | 0 | 0.65 |  |  |  |  | Normal
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0.036881 | 0.023165 | 0.006035 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0.013716 | 0 |  | 2 | [9 empty] | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 50820 | 0 | 0 | 0 | 0.1785 | NA | NA | NA | Sequential | Lognormal
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 26070 | 0 | 0 | 0 | 0.172 | NA | NA | NA | Sequential | Lognormal
HVAC - Boiler capacity | D302 Heat Generating Systems (furnaces and boilers) | 1 | Each | 45 | 45 | 15 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 46200 | 0 | 0 | 0 | 0.18 | NA | NA | NA | Sequential | Lognormal
HVAC - Air Handling Units | D305 Control Panels | 1 | Each | 0 | 0.0066073 | 0.0056634 | 1 | 2 | PFA | 0.25 | 0.25 | NA | NA | 0.4 | 0.4 | NA | NA | 1100 | 32120 | 0 | 0 | 0.1511 | 0.1655 | NA | NA | Mutually exclusive | Lognormal
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 1 | Each | 0 | 0 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 2915 | 0 | 0 | 0 | 0.1394 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0 | 0.007112 | 0 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 3.4285 | 28.6909 | 0 | 0 | 0.256 | 0.0806 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0.01524 | 0.013208 | 0.012192 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 2.3458 | 22.9167 | 0 | 0 | 0.3674 | 0.1002 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.008 | 0.0056667 | 0.003 | 1 | 2 | PFA | 1.3 | NA | NA | NA | 0.4 | NA | NA | NA | 330 | 0 | 0 | 0 | 0.2066 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.0016667 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Normal
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.002 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.004 | 0.006 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0 | 0 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 0.20932 | 1.9127 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0.000508 | 0 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.003556 | 0.001524 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.001524 | 0.001524 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Electrical - Electrical Load | D501 Electrical Service & Distribution | 1 | Each | 3.4747 | 4.6736 | 1.8288 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 1 | Each | 0.06096 | 0.06096 | 0.03048 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 1 | Each | 0 | 0.002032 | 0 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 1 | Each | 0 | 1.3333e-05 | 0 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 1 | Each | 5e-05 | 0.0001 | 5e-05 | 1 | 2 | PFA | 1.01 | NA | NA | NA | 0.6 | NA | NA | NA | 8332.5 | 0 | 0 | 0 | 0.1875 | NA | NA | NA | Sequential | Lognormal
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 1 | Each | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | 2 | PFA | 2.16 | NA | NA | NA | 0.45 | NA | NA | NA | 12057.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 1 | Each | 0.0008 | 0.0003 | 0.0001 | 1 | 2 | PFA | 1.28 | NA | NA | NA | 0.4 | NA | NA | NA | 10202.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0.015 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Standby generators | D509 Other Electrical Systems | 1 | Each | 0 | 0 | 0 | 4 | 2 | PFA | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4 | 0.4 | 220 | 3250 | 600 | 600 | 0.1713 | 0.1705 | 0.1673 | 0.1673 | Mutually exclusive | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 304.8 | 1000 LF | 0.067056 | 0.06096 | 0.033528 | 2 | 2 | PFA | 1.1 | 2.4 | NA | NA | 0.4 | 0.5 | NA | NA | 0.42104 | 3.1879 | 0 | 0 | 0.6488 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 100 | 100 Units | 0.012 | 0.0096667 | 0.008 | 2 | 2 | PFA | 0.75 | 0.95 | NA | NA | 0.4 | 0.4 | NA | NA | 2.75 | 2.75 | 0 | 0 | 0.3665 | 0.3665 | NA | NA | Sequential | Lognormal | Lognormal
Exterenal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0 | 0 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal
Internal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0 | 0 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal

## S
Components | Fragility Database Identifiers | Cost Multiplier (to unit metric) | Quantity unit | RESIDENTIAL - METRIC | COMMERCIAL - METRIC | INDUSTRIAL - METRIC | Damage States | Performance Group | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | Damage Type | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 1 | Each | 0.071535 | 0.040103 | 0.020439 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 1 | Each | 0.013935 | 0.014864 | 9.2903e-05 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.15 | 0.15 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 754 | 0 | 0 | 0 | 0.3 |  |  |  | Mutually exclusive | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.22 | 0.3 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 347 | 0 | 0 | 0 | 0.3
Roofing | B301 Roof Coverings | 9.29 | 100 SF | 0.029729 | 0.030039 | 0.092903 | 2 | 2 | PFA | 0.4 | 0.5 | NA | NA | 0.3 | 0.3 | NA | NA | 132.9386 | 250.2691 | 0 | 0 | 0.5149 | 0.4691 | NA | NA | Sequential | Lognormal | Lognormal
Interior Partitions | C101 Partitions | 120.77 | 1300 SF | 0.036576 | 0.017272 | 0.0009144 | 3 | 1 | PSD | 0.005 | 0.01 | 0.021 | NA | 0.4 | 0.3 | 0.2 | NA | 22.1702 | 56.5124 | 86.9421 | 0 | 0.4814 | 0.5559 | 0.1959 | NA | Sequential | Normal | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 1 | 0.21 | 0.18 | 0.03 | 4 | 1 | PSD | 0.18 | 0.46 | 1.05 | 1.88 | 0.52 | 0.54 | 0.4 | 0.38 | 0.31 | 0.59 | 1.18 | 1.18 | 0.5508 | 0.5183
Ceramic tile walls | C301 Wall Finishes | 1 | Each | 0.011631 | 0.0047915 | 0.00013167 | 1 | 1 | PSD | 0.0021 | NA | NA | NA | 0.6 | NA | NA | NA | 3240 | 0 | 0 | 0 | 0.1542 | NA | NA | NA | Sequential | Lognormal
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.060387 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.088258 | 0.024155 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.0046452 | 0.0040258 | 0.083613 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.0043355 | 0 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Storage Racks | F101 Special Structures including Storage Racks | 15.24 | 50 LF | 0 | 0 | 0.03048 | 2 | 2 | PFA | 0.42 | 0.42 | NA | NA | 0.4 | 0.4 | NA | NA | 15.6471 | 94.1349 | 0 | 0 | 0.3622 | 0.2881 | NA | NA | Mutually exclusive | Lognormal | Lognormal
Stairs | C201 Stairs | 1 | Each | 0.00012 | 0.00010333 | 0 | 3 | 1 | PSD | 0.005 | 0.017 | 0.028 | NA | 0.6 | 0.6 | 0.45 | NA | 280 | 1480 | 9180 | 0 | 0.8015 | 0.5694 | 0.3613 | NA | Sequential | Lognormal | Lognormal | Normal
Elevators | D101 Elevators & Lifts | 1 | Each | 3.4e-05 | 4.7667e-05 | 0 | 4 | 2 | PFA | 0.39 | 0.39 | 0.39 | 0.39 | 0.45 | 0.45 | 0.45 | 0.45 | 1760 | 7480 | 6400 | 1000 | 0.8741 | 0.2776 | 0.4083 | 0.4877 | Simultaneous | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.032309 | 0.015443 | 0.001463 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.004572 | 0.004572 | 0.004572 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.064618 | 0.030886 | 0.0029261 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.009144 | 0.009144 | 0.009144 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Gas supply piping | D301 Energy Supply | 304.8 | 1000 LF | 0.012192 | 0.009652 | 0.004572 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 11.4829 | 0 | 0 | 0 | 0.65 |  |  |  |  | Normal
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0.036881 | 0.023165 | 0.006035 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0.013716 | 0 |  | 2 | [9 empty] | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 50820 | 0 | 0 | 0 | 0.1785 | NA | NA | NA | Sequential | Lognormal
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 26070 | 0 | 0 | 0 | 0.172 | NA | NA | NA | Sequential | Lognormal
HVAC - Boiler capacity | D302 Heat Generating Systems (furnaces and boilers) | 1 | Each | 45 | 45 | 15 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 46200 | 0 | 0 | 0 | 0.18 | NA | NA | NA | Sequential | Lognormal
HVAC - Air Handling Units | D305 Control Panels | 1 | Each | 0 | 0.0066073 | 0.0056634 | 1 | 2 | PFA | 0.25 | 0.25 | NA | NA | 0.4 | 0.4 | NA | NA | 1100 | 32120 | 0 | 0 | 0.1511 | 0.1655 | NA | NA | Mutually exclusive | Lognormal
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 1 | Each | 0 | 0 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 2915 | 0 | 0 | 0 | 0.1394 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0 | 0.007112 | 0 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 3.4285 | 28.6909 | 0 | 0 | 0.256 | 0.0806 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0.01524 | 0.013208 | 0.012192 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 2.3458 | 22.9167 | 0 | 0 | 0.3674 | 0.1002 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.008 | 0.0056667 | 0.003 | 1 | 2 | PFA | 1.3 | NA | NA | NA | 0.4 | NA | NA | NA | 330 | 0 | 0 | 0 | 0.2066 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.0016667 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Normal
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.002 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.004 | 0.006 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0 | 0 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 0.20932 | 1.9127 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0.000508 | 0 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.003556 | 0.001524 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.001524 | 0.001524 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Electrical - Electrical Load | D501 Electrical Service & Distribution | 1 | Each | 3.4747 | 4.6736 | 1.8288 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 1 | Each | 0.06096 | 0.06096 | 0.03048 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 1 | Each | 0 | 0.002032 | 0 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 1 | Each | 0 | 1.3333e-05 | 0 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 1 | Each | 5e-05 | 0.0001 | 5e-05 | 1 | 2 | PFA | 1.01 | NA | NA | NA | 0.6 | NA | NA | NA | 8332.5 | 0 | 0 | 0 | 0.1875 | NA | NA | NA | Sequential | Lognormal
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 1 | Each | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | 2 | PFA | 2.16 | NA | NA | NA | 0.45 | NA | NA | NA | 12057.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 1 | Each | 0.0008 | 0.0003 | 0.0001 | 1 | 2 | PFA | 1.28 | NA | NA | NA | 0.4 | NA | NA | NA | 10202.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0.015 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Standby generators | D509 Other Electrical Systems | 1 | Each | 0 | 0 | 0 | 4 | 2 | PFA | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4 | 0.4 | 220 | 3250 | 600 | 600 | 0.1713 | 0.1705 | 0.1673 | 0.1673 | Mutually exclusive | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 304.8 | 1000 LF | 0.067056 | 0.06096 | 0.033528 | 2 | 2 | PFA | 1.1 | 2.4 | NA | NA | 0.4 | 0.5 | NA | NA | 0.42104 | 3.1879 | 0 | 0 | 0.6488 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 100 | 100 Units | 0.012 | 0.0096667 | 0.008 | 2 | 2 | PFA | 0.75 | 0.95 | NA | NA | 0.4 | 0.4 | NA | NA | 2.75 | 2.75 | 0 | 0 | 0.3665 | 0.3665 | NA | NA | Sequential | Lognormal | Lognormal
Exterenal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0.28228 | 0.20172 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal
Internal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0.11919 | 0.074816 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal

## T
Components | Fragility Database Identifiers | Cost Multiplier (to unit metric) | Quantity unit | RESIDENTIAL - METRIC | COMMERCIAL - METRIC | INDUSTRIAL - METRIC | Damage States | Performance Group | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | Damage Type | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 1 | Each | 0.071535 | 0.040103 | 0.020439 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 1 | Each | 0.013935 | 0.014864 | 9.2903e-05 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.15 | 0.15 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 754 | 0 | 0 | 0 | 0.3 |  |  |  | Mutually exclusive | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.22 | 0.3 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 347 | 0 | 0 | 0 | 0.3
Roofing | B301 Roof Coverings | 9.29 | 100 SF | 0.029729 | 0.030039 | 0.092903 | 2 | 2 | PFA | 0.4 | 0.5 | NA | NA | 0.3 | 0.3 | NA | NA | 132.9386 | 250.2691 | 0 | 0 | 0.5149 | 0.4691 | NA | NA | Sequential | Lognormal | Lognormal
Interior Partitions | C101 Partitions | 120.77 | 1300 SF | 0.036576 | 0.017272 | 0.0009144 | 3 | 1 | PSD | 0.005 | 0.01 | 0.021 | NA | 0.4 | 0.3 | 0.2 | NA | 22.1702 | 56.5124 | 86.9421 | 0 | 0.4814 | 0.5559 | 0.1959 | NA | Sequential | Normal | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 1 | 0.21 | 0.18 | 0.03 | 4 | 1 | PSD | 0.18 | 0.46 | 1.05 | 1.88 | 0.52 | 0.54 | 0.4 | 0.38 | 0.31 | 0.59 | 1.18 | 1.18 | 0.5508 | 0.5183
Ceramic tile walls | C301 Wall Finishes | 1 | Each | 0.011631 | 0.0047915 | 0.00013167 | 1 | 1 | PSD | 0.0021 | NA | NA | NA | 0.6 | NA | NA | NA | 3240 | 0 | 0 | 0 | 0.1542 | NA | NA | NA | Sequential | Lognormal
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.060387 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.088258 | 0.024155 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.0046452 | 0.0040258 | 0.083613 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.0043355 | 0 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Storage Racks | F101 Special Structures including Storage Racks | 15.24 | 50 LF | 0 | 0 | 0.03048 | 2 | 2 | PFA | 0.42 | 0.42 | NA | NA | 0.4 | 0.4 | NA | NA | 15.6471 | 94.1349 | 0 | 0 | 0.3622 | 0.2881 | NA | NA | Mutually exclusive | Lognormal | Lognormal
Stairs | C201 Stairs | 1 | Each | 0.00012 | 0.00010333 | 0 | 3 | 1 | PSD | 0.005 | 0.017 | 0.028 | NA | 0.6 | 0.6 | 0.45 | NA | 280 | 1480 | 9180 | 0 | 0.8015 | 0.5694 | 0.3613 | NA | Sequential | Lognormal | Lognormal | Normal
Elevators | D101 Elevators & Lifts | 1 | Each | 3.4e-05 | 4.7667e-05 | 0 | 4 | 2 | PFA | 0.39 | 0.39 | 0.39 | 0.39 | 0.45 | 0.45 | 0.45 | 0.45 | 1760 | 7480 | 6400 | 1000 | 0.8741 | 0.2776 | 0.4083 | 0.4877 | Simultaneous | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.032309 | 0.015443 | 0.001463 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.004572 | 0.004572 | 0.004572 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.064618 | 0.030886 | 0.0029261 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.009144 | 0.009144 | 0.009144 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Gas supply piping | D301 Energy Supply | 304.8 | 1000 LF | 0.012192 | 0.009652 | 0.004572 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 11.4829 | 0 | 0 | 0 | 0.65 |  |  |  |  | Normal
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0.036881 | 0.023165 | 0.006035 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0.013716 | 0 |  | 2 | [9 empty] | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 50820 | 0 | 0 | 0 | 0.1785 | NA | NA | NA | Sequential | Lognormal
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 26070 | 0 | 0 | 0 | 0.172 | NA | NA | NA | Sequential | Lognormal
HVAC - Boiler capacity | D302 Heat Generating Systems (furnaces and boilers) | 1 | Each | 45 | 45 | 15 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 46200 | 0 | 0 | 0 | 0.18 | NA | NA | NA | Sequential | Lognormal
HVAC - Air Handling Units | D305 Control Panels | 1 | Each | 0 | 0.0066073 | 0.0056634 | 1 | 2 | PFA | 0.25 | 0.25 | NA | NA | 0.4 | 0.4 | NA | NA | 1100 | 32120 | 0 | 0 | 0.1511 | 0.1655 | NA | NA | Mutually exclusive | Lognormal
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 1 | Each | 0 | 0 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 2915 | 0 | 0 | 0 | 0.1394 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0 | 0.007112 | 0 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 3.4285 | 28.6909 | 0 | 0 | 0.256 | 0.0806 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0.01524 | 0.013208 | 0.012192 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 2.3458 | 22.9167 | 0 | 0 | 0.3674 | 0.1002 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.008 | 0.0056667 | 0.003 | 1 | 2 | PFA | 1.3 | NA | NA | NA | 0.4 | NA | NA | NA | 330 | 0 | 0 | 0 | 0.2066 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.0016667 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Normal
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.002 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.004 | 0.006 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0 | 0 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 0.20932 | 1.9127 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0.000508 | 0 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.003556 | 0.001524 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.001524 | 0.001524 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Electrical - Electrical Load | D501 Electrical Service & Distribution | 1 | Each | 3.4747 | 4.6736 | 1.8288 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 1 | Each | 0.06096 | 0.06096 | 0.03048 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 1 | Each | 0 | 0.002032 | 0 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 1 | Each | 0 | 1.3333e-05 | 0 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 1 | Each | 5e-05 | 0.0001 | 5e-05 | 1 | 2 | PFA | 1.01 | NA | NA | NA | 0.6 | NA | NA | NA | 8332.5 | 0 | 0 | 0 | 0.1875 | NA | NA | NA | Sequential | Lognormal
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 1 | Each | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | 2 | PFA | 2.16 | NA | NA | NA | 0.45 | NA | NA | NA | 12057.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 1 | Each | 0.0008 | 0.0003 | 0.0001 | 1 | 2 | PFA | 1.28 | NA | NA | NA | 0.4 | NA | NA | NA | 10202.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0.015 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Standby generators | D509 Other Electrical Systems | 1 | Each | 0 | 0 | 0 | 4 | 2 | PFA | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4 | 0.4 | 220 | 3250 | 600 | 600 | 0.1713 | 0.1705 | 0.1673 | 0.1673 | Mutually exclusive | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 304.8 | 1000 LF | 0.067056 | 0.06096 | 0.033528 | 2 | 2 | PFA | 1.1 | 2.4 | NA | NA | 0.4 | 0.5 | NA | NA | 0.42104 | 3.1879 | 0 | 0 | 0.6488 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 100 | 100 Units | 0.012 | 0.0096667 | 0.008 | 2 | 2 | PFA | 0.75 | 0.95 | NA | NA | 0.4 | 0.4 | NA | NA | 2.75 | 2.75 | 0 | 0 | 0.3665 | 0.3665 | NA | NA | Sequential | Lognormal | Lognormal
Exterenal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0 | 0 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal
Internal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0 | 0 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal

## ADO
Components | Fragility Database Identifiers | Cost Multiplier (to unit metric) | Quantity unit | RESIDENTIAL - METRIC | COMMERCIAL - METRIC | INDUSTRIAL - METRIC | Damage States | Performance Group | Engineering Demand Parameter | DS1, Median Demand | DS2, Median Demand | DS3, Median Demand | DS4, Median Demand | DS1, Total Dispersion (Beta) | DS2, Total Dispersion (Beta) | DS3, Total Dispersion (Beta) | DS4, Total Dispersion (Beta) | DS1, Repair COST | DS2, Repair COST | DS3, Repair COST | DS4, Repair COST | DS1, COST Dispersion (Beta) | DS2, COST Dispersion (Beta) | DS3, COST Dispersion (Beta) | DS4, COST Dispersion (Beta) | Damage Type | DS1, best fit | DS2, best fit | DS3, best fit | DS4, best fit
Cladding - Gross Wall Area | B401 Exterior Finishes | 1 | Each | 0.071535 | 0.040103 | 0.020439 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Cladding - Windows & Glazing Area | B202 Exterior Window Systems | 1 | Each | 0.013935 | 0.014864 | 9.2903e-05 | 2 | 1 | PSD | 0.0338 | 0.0383 | NA | NA | 0.4 | 0.4 | NA | NA | 102.75 | 102.75 | 0 | 0 | 0.17 | 0.17 | NA | NA | Sequential | Lognormal | Lognormal
Doors | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.15 | 0.15 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 754 | 0 | 0 | 0 | 0.3 |  |  |  | Mutually exclusive | Lognormal
Windows | O'Reilly et al., Shahnazaryan et al. | 1 | Each | 0.22 | 0.3 | 0.15 | 1 | 1 | PSD | 1.88 | NA | NA | NA | 0.38 | NA | NA | NA | 347 | 0 | 0 | 0 | 0.3
Roofing | B301 Roof Coverings | 9.29 | 100 SF | 0 | 0 | 0 | 2 | 2 | PFA | 0.4 | 0.5 | NA | NA | 0.3 | 0.3 | NA | NA | 132.9386 | 250.2691 | 0 | 0 | 0.5149 | 0.4691 | NA | NA | Sequential | Lognormal | Lognormal
Interior Partitions | C101 Partitions | 120.77 | 1300 SF | 0.036576 | 0.017272 | 0.0009144 | 3 | 1 | PSD | 0.005 | 0.01 | 0.021 | NA | 0.4 | 0.3 | 0.2 | NA | 22.1702 | 56.5124 | 86.9421 | 0 | 0.4814 | 0.5559 | 0.1959 | NA | Sequential | Normal | Lognormal | Lognormal
Gypsum Partitions | Sassun et al. | 1 | 1 | 0.21 | 0.18 | 0.03 | 4 | 1 | PSD | 0.18 | 0.46 | 1.05 | 1.88 | 0.52 | 0.54 | 0.4 | 0.38 | 0.31 | 0.59 | 1.18 | 1.18 | 0.5508 | 0.5183
Ceramic tile walls | C301 Wall Finishes | 1 | Each | 0.011631 | 0.0047915 | 0.00013167 | 1 | 1 | PSD | 0.0021 | NA | NA | NA | 0.6 | NA | NA | NA | 3240 | 0 | 0 | 0 | 0.1542 | NA | NA | NA | Sequential | Lognormal
Ceilings - Lay in Tile | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.060387 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Gypsum board | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.088258 | 0.024155 | 0.0046452 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0.0046452 | 0.0040258 | 0.083613 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Ceilings - Other (high end) | C303 Ceilings and Ceiling Lighting | 119.84 | 1290 SF | 0 | 0.0043355 | 0 | 3 | 2 | PFA | 0.86 | 1.3275 | 1.5625 | NA | 0.25 | 0.25 | 0.25 | NA | 18.6937 | 146.3264 | 301.0326 | 0 | 0.5508 | 0.5183 | 0.2026 | NA | Sequential | Normal | Lognormal | Lognormal
Storage Racks | F101 Special Structures including Storage Racks | 15.24 | 50 LF | 0 | 0 | 0.03048 | 2 | 2 | PFA | 0.42 | 0.42 | NA | NA | 0.4 | 0.4 | NA | NA | 15.6471 | 94.1349 | 0 | 0 | 0.3622 | 0.2881 | NA | NA | Mutually exclusive | Lognormal | Lognormal
Stairs | C201 Stairs | 1 | Each | 0 | 0 | 0 | 3 | 1 | PSD | 0.005 | 0.017 | 0.028 | NA | 0.6 | 0.6 | 0.45 | NA | 280 | 1480 | 9180 | 0 | 0.8015 | 0.5694 | 0.3613 | NA | Sequential | Lognormal | Lognormal | Normal
Elevators | D101 Elevators & Lifts | 1 | Each | 0 | 0 | 0 | 4 | 2 | PFA | 0.39 | 0.39 | 0.39 | 0.39 | 0.45 | 0.45 | 0.45 | 0.45 | 1760 | 7480 | 6400 | 1000 | 0.8741 | 0.2776 | 0.4083 | 0.4877 | Simultaneous | Lognormal | Normal | Normal | Normal
Piping - Cold Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.032309 | 0.015443 | 0.001463 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Cold Domestic Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.004572 | 0.004572 | 0.004572 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.064618 | 0.030886 | 0.0029261 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Hot Domestic Waster Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.009144 | 0.009144 | 0.009144 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.4 | 0.4 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Gas supply piping | D301 Energy Supply | 304.8 | 1000 LF | 0.012192 | 0.009652 | 0.004572 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 11.4829 | 0 | 0 | 0 | 0.65 |  |  |  |  | Normal
Piping - Sanitary Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0.036881 | 0.023165 | 0.006035 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping - 2 ½ inch diameter or smaller | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Process Piping – greater than 2 ½ diameter | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0 | 0 | 1 | 2 | PFA | 2.25 | NA | NA | NA | 0.5 | NA | NA | NA | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential | Normal
Piping - Acid Waste Piping | D203 Sanitary Waste Piping System | 304.8 | 1000 LF | 0 | 0.013716 | 0 |  | 2 | [9 empty] | 4.3963 | 0 | 0 | 0 | 0.3142 | NA | NA | NA | Sequential
HVAC - Chiller capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 50820 | 0 | 0 | 0 | 0.1785 | NA | NA | NA | Sequential | Lognormal
HVAC - Cooling Tower capacity | D303 Chillers, Cooling Towers and Compressors | 1 | Each | 0 | 0.00028956 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 26070 | 0 | 0 | 0 | 0.172 | NA | NA | NA | Sequential | Lognormal
HVAC - Boiler capacity | D302 Heat Generating Systems (furnaces and boilers) | 1 | Each | 45 | 45 | 15 | 1 | 2 | PFA | 0.2 | NA | NA | NA | 0.4 | NA | NA | NA | 46200 | 0 | 0 | 0 | 0.18 | NA | NA | NA | Sequential | Lognormal
HVAC - Air Handling Units | D305 Control Panels | 1 | Each | 0 | 0.0066073 | 0.0056634 | 1 | 2 | PFA | 0.25 | 0.25 | NA | NA | 0.4 | 0.4 | NA | NA | 1100 | 32120 | 0 | 0 | 0.1511 | 0.1655 | NA | NA | Mutually exclusive | Lognormal
HVAC - Fans | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 1 | Each | 0 | 0 | 0 | 1 | 2 | PFA | 0.5 | NA | NA | NA | 0.4 | NA | NA | NA | 2915 | 0 | 0 | 0 | 0.1394 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC Ducts – 6 sq. feet for larger | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0 | 0.007112 | 0 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 3.4285 | 28.6909 | 0 | 0 | 0.256 | 0.0806 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC Ducts – less than 6 sq. feet | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 304.8 | 1000 LF | 0.01524 | 0.013208 | 0.012192 | 2 | 2 | PFA | 1.5 | 2.25 | NA | NA | 0.4 | 0.4 | NA | NA | 2.3458 | 22.9167 | 0 | 0 | 0.3674 | 0.1002 | NA | NA | Sequential | Lognormal | Lognormal
HVAC - HVAC in-line Drops & Diffusers | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.008 | 0.0056667 | 0.003 | 1 | 2 | PFA | 1.3 | NA | NA | NA | 0.4 | NA | NA | NA | 330 | 0 | 0 | 0 | 0.2066 | NA | NA | NA | Sequential | Lognormal
HVAC - HVAC in-line Coils | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.0016667 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Normal
HVAC - VAV Boxes | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0 | 0.002 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
HVAC - Fan Coil Unis | D304 Distribution System including Fans, Drops & Diffusers and VAV Boxes | 10 | 10 Units | 0.004 | 0.006 | 0 | 1 | 2 | PFA | 1.9 | NA | NA | NA | 0.4 | NA | NA | NA | 1650 | 0 | 0 | 0 | 0.2942 | NA | NA | NA | Sequential | Lognormal
Piping - Steam & Chilled Water Piping - 2 ½ inch diameter or smaller | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0 | 0 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 0.20932 | 1.9127 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Steam & Chilled Water Piping – greater than 2 ½ diameter | D206 Steam Piping | 304.8 | 1000 LF | 0 | 0.000508 | 0 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping - 2 ½ inch diameter or smaller | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.003556 | 0.001524 | 2 | 2 | PFA | 0.55 | 1.1 | NA | NA | 0.5 | 0.5 | NA | NA | 1.0466 | 9.5636 | 0 | 0 | 0.7637 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Piping - Heating Water Piping – greater than 2 ½ diameter | D202 Domestic Water Distribution including hot water heaters | 304.8 | 1000 LF | 0.001524 | 0.001524 | 0.001524 | 2 | 2 | PFA | 1.5 | 2.6 | NA | NA | 0.5 | 0.5 | NA | NA | 0.45932 | 4.3963 | 0 | 0 | 0.6488 | 0.4038 | NA | NA | Sequential | Lognormal | Lognormal
Electrical - Electrical Load | D501 Electrical Service & Distribution | 1 | Each | 3.4747 | 4.6736 | 1.8288 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Electrical Distribution conduits | D502 Lighting and Branch Wiring | 1 | Each | 0.06096 | 0.06096 | 0.03048 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Electrical Distribution – cable trays | D502 Lighting and Branch Wiring | 1 | Each | 0 | 0.002032 | 0 | 1 | 2 | PFA | 1 | NA | NA | NA | 0.4 | NA | NA | NA | 12.1458 | 0 | 0 | 0 | 0.2 |  |  |  | Mutually exclusive | Lognormal
Electrical - Motor Control Centers | D501 Electrical Service & Distribution | 1 | Each | 0 | 1.3333e-05 | 0 | 1 | 2 | PFA | 0.73 | NA | NA | NA | 0.45 | NA | NA | NA | 4565 | 0 | 0 | 0 | 0.1826 | NA | NA | NA | Sequential | Lognormal
Electrical - Transformers < 100kVA | D501 Electrical Service & Distribution | 1 | Each | 5e-05 | 0.0001 | 5e-05 | 1 | 2 | PFA | 1.01 | NA | NA | NA | 0.6 | NA | NA | NA | 8332.5 | 0 | 0 | 0 | 0.1875 | NA | NA | NA | Sequential | Lognormal
Electrical - Distribution Panel | D501 Electrical Service & Distribution | 1 | Each | 1.3e-05 | 3.3333e-05 | 2e-05 | 1 | 2 | PFA | 2.16 | NA | NA | NA | 0.45 | NA | NA | NA | 12057.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Wall mounted switchgear | D501 Electrical Service & Distribution | 1 | Each | 0.0008 | 0.0003 | 0.0001 | 1 | 2 | PFA | 1.28 | NA | NA | NA | 0.4 | NA | NA | NA | 10202.5 | 0 | 0 | 0 | 0.1572 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Lay in fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Lighting Fixtures – Stem hung fluorescent | C303 Ceilings | 1 | Each | 0 | 0.01 | 0.015 | 1 | 2 | PFA | 0.6 | NA | NA | NA | 0.4 | NA | NA | NA | 0.46 | 0 | 0 | 0 | 0.6369 | NA | NA | NA | Sequential | Lognormal
Electrical - Standby generators | D509 Other Electrical Systems | 1 | Each | 0 | 0 | 0 | 4 | 2 | PFA | 0.9 | 0.9 | 0.9 | 0.9 | 0.4 | 0.4 | 0.4 | 0.4 | 220 | 3250 | 600 | 600 | 0.1713 | 0.1705 | 0.1673 | 0.1673 | Mutually exclusive | Lognormal | Lognormal | Lognormal | Lognormal
Fire Protection - Sprinkler Piping | D401 Sprinkler Horizontal Distribution including Risers and Drops | 304.8 | 1000 LF | 0 | 0 | 0 | 2 | 2 | PFA | 1.1 | 2.4 | NA | NA | 0.4 | 0.5 | NA | NA | 0.42104 | 3.1879 | 0 | 0 | 0.6488 | 0.4054 | NA | NA | Sequential | Lognormal | Lognormal
Fire Protection - Sprinkler Drops | D401 Sprinkler Horizontal Distribution including Risers and Drops | 100 | 100 Units | 0 | 0 | 0 | 2 | 2 | PFA | 0.75 | 0.95 | NA | NA | 0.4 | 0.4 | NA | NA | 2.75 | 2.75 | 0 | 0 | 0.3665 | 0.3665 | NA | NA | Sequential | Lognormal | Lognormal
Exterenal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0 | 0 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal
Internal Parititioning - Masonry Infills | De Risi et al, Cardone and Perrone | 1 | 1 | 0 | 0 | 0 | 4 | 1 | PSD | 0.0992 | 0.4092 | 1.2028 | 2.1328 | 0.8 | 0.4 | 0.4 | 0.4 | 0.30351 | 0.5268 | 1.793 | 1.9884 | 0.55 | 0.55 | 0.55 | 0.55 | Sequential | Lognormal | Lognormal | Lognormal | Lognormal